## COPPER HOT WATER
WATER MANAGEMENT / FIXTURE FLUSHING
DATE: | 2019-07-11 | [6 empty] | TECH: | TRPoole
Burn Times | Area to Flush | # | Time | Temp 1 Min | Temp 5 Min | Residual PPM | Temp 15 Min | Residual PPM | Total Flush Time
2030 - 2100 | SG Return |  | 7:45 | 120 | 120 | 0.27 | 120 | 0.09
2230 - 2300 | 6th Fl Med Surg N |  | 8:00 | 122.3 | 122.2 | 0.05 | 125.2 | 0.05
0030 - 0100 | 6th Fl Med Surg S |  | :
0230 - 0300 | 6th Fl Med Surg WR |  | 8:30 | 120.2 | 121.9 | 0.05 | 122.6 | 0.06
0430 - 0500 | 4th Fl Med Surg |  | :
0630 - 0700 | 4 West / CCD A |  | 13:00 | 120.8 | 123.1 | 0.04 | 123 | 0
| 4 West / CCD B |  | 13:30 | 121.5 | 122.9 | 0.05 | 122.2 | 0.02
| 3rd Fl - ASU |  | :
| 2nd Fl - Endo |  | :
| Emergency Dept A |  | :
| Emergency Dept B |  | :
| 1 - North Wing |  | :
NOTES / COMMENTS
10/25/2018: NEW CYLINDERS - 12/11/2018: CHRIS GAUTHIER - NEW BURN TIMES , AMPERAGE CHANGE 4.0 TO 3.5A - 12/20/2018: CYLINDERS CLEANED. - 01/16/2019: AMPS ADJ
3.5 TO 3.75A. - 01/18/2019: CYLINDERS CLEANED. 01/24/2019: NEW CYLINDERS ORDERED. - 01/26/2019: CYLINDERS CLEANED WITH LIME SLAYER. - 02/01/2019: NEW CYLINDERS
INSTALLED. 03/04/2019: INSTALLED SOCK FILTER ON HOT WATER LOOP. 03/18/2019: NEW SOCK FILTER INSTALLED - JW. 03/28/2019: REPLACED SOCK FILTER - TRP.
04/11/2019: REPLACED SOCK FILTER - TRP 04/26/2019: REPLACED SOCK FILTER - TRP. 05/07/2019: REPLACED SOCK FILTER - JW. 06/11/2019: NEW CYLINDERS INSTALLED - JW.
DECONTAMINATION SHOWERS
| Location |  | Time | Decon 1 | Decon 2 | Mixing Valve Temp |  | Notes
| Temp 5 Min |  | :
| Temp 20 Min |  | :

## CL2 COLD WATER
4 | # | Time | Oxygen Reduction |  | Water Flow |  | Chlorine Dioxide MG/L (>.25) |  |  |  | Comments
|  |  | Potential (ORP) |  | GPM |  | Meter |  | Water Sample
Cold Water Supply |  | :
Location | # | Time | Cold Water Temp *F |  |  |  | Chlorine Dioxide MG/L (>.25) |  |  |  | Comments
3 - 4 SAMPLES - 5 MIN INT------> |  |  | A | B | C | D | A | B | C | D
6th Fl Med Surg N |  | :
6th Fl Med Surg S |  | :
6th Fl Med Surg WR |  | :
4th Fl Med Surg |  | :
4 West / CCD A |  | :
4 West / CCD B |  | :
3rd Fl - ASU |  | :
2nd Fl - Endo |  | :
Emergency Dept. A |  | :
Emergency Dept. B |  | :
1 - North Wing |  | :
01/18/2019: CL2 UNIT OFF (May be depleting copper levels on Hot Water) 01/22/2019: CL2 UNIT BACK ON @ 09:15. 02/01/2019: CL2 UNIT OFF. 03/01/2019: CL2 System in Service.